## Sheet1
S.No. | Items Details | Make | Qty | Unit | Rate
1 | Pendent Type 15 mm dia quartzoid bulb type brass sprinklers of rating 68 degree with required accessories. | ( MAKE: TYCO) | 1500 | Nos
2 | UP RIGHT Type 15 mm dia quartzoid bulb type brass sprinklers of rating 68 degree with required accessories. | ( MAKE: TYCO) | 200 | Nos
3 | Side Wall Type 15 mm dia quartzoid bulb type brass sprinklers of rating 68 degree with required accessories. | ( MAKE: TYCO) | 20 | Nos
4 | Water curtain nozzle 15 mm dia nickel chrome plated brass , BSPT , K- factor as per design consideration complete as required. | ( MAKE: TYCO) | 200 | Nos
5 | S.S. Sprinkler flexible pipe 1500 mm (UL listed) complete with 15 PT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (BURST) with branch line (inlet) 25 mm NPT male thread to sprinkler head (outlet ) 15 mm NPT female thread with reducer , nipple , 2 side brackets , center bracket, stockbar of following sizes complite as required. |  | 100 | Nos
6 | Single headed internal and external yard hydrant valve with instantaneous Stainless Steel coupling of 63 mm dia with cast iron wheel ISI marked conforming to IS 5290 ( TYPE -A ) with blank stainless steel cap and chain as required. | Lifeguard | 25 | Nos
7 | INTERNAL OR EXTERNAL weather proof standard fire hose cabinet (750 mm x 600 mm x 250 mm deep) for yard hydrants made of 16 SWG powder coated M.S. sheet having single or double opening glazed (4.0 mm thick glass) shutter including necessary locking arrangement by allan key, stove enamelled Fire red finish with " Fire Hose" marked on front, suitable for housing 2 nos. Hose pipe, 1 No. branch pipe & nozzle spanner. | Lifeguard | 25 | Nos
8 | 63 mm dia ,15 m long RRL hose pipe with 63 mm dia male and femaile coupling duly bond with GI WIRE , RIVETS ETC . CONFORMING TO IS 636 (Type -A ) as required. | Lifeguard | 50 | Nos
9 | 63 mm dia Stainless Steel (grade 304) short branch pipe with 20 mm nominal internal diameter size nozzle conforming to IS 903 sutitable for instantaneous connection pipe coupling as required. | Lifeguard | 25 | Nos
10 | First-aid Hos Reel Drum with MS construction spray painted in post office red, conforming to IS 884 complite with the follwing as required. 20 mm nominal internal dia water hose thermoplastic (Textile reinforced ) type-2 as per IS 12585. 20 mm normal internal dia gun metal globe & nozzle. Drum and brackets for fixing the equipmets on wall.connections from riser with 25 mm dia stop gunmetal valve & MS pipe and socket. | Lifeguard | 25 | Nos
11 | Fire brigade connection of cast iron body with gun metal male instantaneous inlet couplings complete with cap and chain as reqd , for sutitable dia MS pipe connection conforming to IS 904 AS REQUIRED. 4 WAY -150 mm dia MS pipe. | Lifeguard | 1 | Nos
12 | Stainless steel Y- strainer fabricated out of 1.6 mm thick stainless steel, grade 304 , sheet with 3 mm dia hole with stainless steel flange . 250 mm dia. | DRP/zoloto | 2 | Nos
13 | Stainless steel Y- strainer fabricated out of 1.6 mm thick stainless steel, grade 304 , sheet with 3 mm dia hole with stainless steel flange . 150 mm dia. | DRP/zoloto | 2 | Nos
14 | Air vessel made of 250 mm dia ,8 mm thick MS sheet, 1200 mm in height with air release valve on top and flanged connection to riser, drain arrangement with 25 mm dia gun metal wheel valve with required accessories, pressure gauge and paintingwith synthetic enamel paint of approved shade as required . | Lifeguard | 10 | Nos
15 | Pressure switch in M.S pipe line including connection. | MAKE INDIFUS/DANFOSE | 10 | Nos
16 | Fire brigade draw off connection confirming to IS : 4038-1986 with 150 mm Non return valve/ strainer incluiding necessary fittings the word FIRE BRIGADE DRAW OFF to be painted on the box complete all as specified and directed. | Lifeguard
17 | 100 mm dia Burden type, Stainless Steel dial type pressure gauge (in Pump Room) including brass isolation valve and pipe having caliberation of 0-15 Kg/cm2. | MAKE H.GURU/FIEBIG | 3 | Nos
18 | 100 mm dia Burden type, Stainless Steel dial type pressure switch (in Pump Room) including brass isolation valve and pipe having caliberation of 0-15 Kg/cm2. | MAKE H.GURU/FIEBIG | 5 | Nos
19 | Flow switch in following sizes M.S pipe including connection etc as required . 150 mm dia. | System Sensor/ HD/ NEWAGE | 4 | Nos
20 | Portable Co2 fire extinguisher of capacity 4.5 kg flat base including valve, dischargeone metar long hose of. ISI MARK 15683). | Lifeguard | 25 | Nos
21 | Portable ABC multipurpose filled by 90% (MAP ) mono amonioum phosphate powder , nitrogen pressurised type fire extinguisher, Capacity 6 kg with 90% map complete in all resp. | Lifeguard | 25 | Nos
22 | Fire Extinguisher 2 KG, Clean Agent type ISI mark IS code 15683 | Lifeguard | 10 | Nos
23 | Fire Extinguisher 5 kg modular type self operated on 68o temperature Clean Agent type CE certified filled with NAFPIV clean agent gas. | Lifeguard | 10 | Nos
24 | Fire Extinguisher 50 KG DCP (Dry Chemical Powder) Trolley type fire extinguisher as per IS 16018I jet length minimum 8 mtr minimum discharge time 40-50 sec,tested on 30 kgf/cm2. | Lifeguard | 5 | Nos
25 | AFFF foam type fire extinguisher, Capacity 9 liter complete in all resp SITC ISI marked (IS: 15683) portable. | Lifeguard | 2 | Nos
26 | Portable Co2 fire extinguisher of capacity 22.5 kg flat base including valve discharge hose of not less than 10mm dia. meter complete in all respect including initial fill with Co2 gas confirming to IS 307-1966 and filled to filling ratio of not more than 0.367. | Lifeguard | 2 | Nos
27 | 50 KG Mechanical Foam AFFF Trolley type fire extinguisher as per IS 16018 jet length minimum 10 mtr minimum discharge time 60-180 sec,tested on 35 kgf/cm2 with 2 kg co2 external fire extinguisher. | Lifeguard | 4 | Nos
28 | Water Monitor to discharge 1750 LPM, 7 kg/cm2 & 55 meter throw range. | Lifeguard | 2 | Nos
29 | 150mm dia.hydraulically operated 150 mm dia. Sprinkler control valve, with water motor gong bell and trims as required, pressure gauges, drain valves, ball valves, check valves, strainers etc. complete. Alarm valve shall be UL Listed. | Lifeguard | 2 | Nos
30 | chemcial powder (ABC) type fire extinguisher fitted with Co2 gas cartridge as per IS:15683. Capacity - 6.0 kgs | Lifeguard | 30 | Nos
31 | chemcial powder (ABC) type fire extinguisher fitted with Co2 gas cartridge as per IS:15683. Capacity - 9.0 kgs | Lifeguard | 24 | Nos
32 | trolley mounted with external Co2 cylinder. Capacity - 50.0 kgs | Lifeguard | 2 | Nos
33 | Water type fire extinguisher fitted with Co2 gas cartridge as per IS:15683. Capacity - 9.0 Liter | Lifeguard | 12 | Nos
34 | Water type fire extinguisher fitted with Co2 gas cartridge as per IS:15683. Capacity - 50 Liter | Lifeguard | 2 | Nos
35 | Co2 Type fire extinguisher as per IS:15683. Capacity - 4.5 Kgs | Lifeguard | 4 | Nos
36 | Trolley Mounted Co2 Type fire extinguisher as per IS:15683. Capacity - 9.2 Kgs | Lifeguard | 2 | Nos
37 | Trolley Mounted Co2 Type fire extinguisher as per IS:15683. Capacity - 25 Kgs | Lifeguard | 4 | Nos
38 | Mechanical Foam cartridge type as per IS:15683. Capacity - 9.0 Liter | Lifeguard | 4 | Nos
39 | ABC powder Modular automatic type fire extinguisher (ceiling mounting). | Lifeguard | 6 | Nos
40
41 | Air Vessel of continuous welded construction with flanged discharge header on the top of each riser fabricated out of 8 mm thick MS sheet, Air Release Valve complete with suitable drain arrangement with 25 mm dia gun metal ball valve complete with all accessories etc. pressure gauge, synthetic enamel paint of approved shade as required of the following sizes | Lifeguard
42 | 1.2 Meter high and 250 mm dia |  | 3 | Nos
43 | Fabricating Air Vessel of continuous welded construction with flanged discharge header in pump house fabricated out of 10 mm thick dished ends and 8 mm thick MS sheet, Air Release Valve, complete with drain arrangement with 25 mm dia gun metal wheel valve complete with all accessories etc. as required of the following sizes: | Lifeguard
44 | 2 Meter high and 450 mm dia suitable to operate Jockey Pump, Main Fire Pump & Diesel Engine Driven Fire Pump |  | 2
45 | single gunmetal suction collecting head as per IS: 904-1983, hose coupling (draw out connection) with female outlet as per 903 complete with 150 mm dia. G.I. Suction pipe (with puddle flange) with a foot valve with strainer complete as per drawings. | LifeGuard | 1
46 | Providing 25 mm dia inspection & testing assembly with gun metal ball valve, gun metal sight glass, drain valve (Ball valve 50mm dia) & connection to drain. | Zoloto,DRP | 6
47 | Orifice Plate made of 6 mm thick, stainless steel with orifice of required size in between flange & landing valve of external and internal hydrant to reduce pressure to working pressure of 3.5 Kg / cm2 complete. | LifeGuard | 20
48 | double flanged Metallic expansion with M.S. fixed flanges (PN-1.6) joint (suitable for system test pressure) of standard length as per manufacturers specs including rubber gaskets, flanges, nuts, bolts and washers complete. | syflex/ Resistoflex
| 150 mm dia |  | 8
| 65 mm dia |  | 2